深圳市永亿豪电子有限公司

APPROVAL SHEET

Customer:

Customer P/N:

SNOWFAN Model NO.:              YY8025H24B

SNOWFAN P/N:

Version.:        0               Sample NO.:

Issue date:  2019-7-22            Quantity:   0   PCS

*Please sign back this specification for our record upon your approval. Thanks!

| Company Stamp |  | Customer approval Stamp |
| --- | --- | --- |
| 制作：程 梅 |  | 承认： |
| 复核：刘新华 |  | 核准： |
| 核准： |  | 日期： |

地址:深圳市龙华新区观澜街道福民茜坑新村佰公坳工业区二巷10号厂房电话：28035708   传真：28035808

http://www.snowfan.com.cn/   E-Mail: yongyihao@snowfan.com.cn

| 版次 | 变更履历 | 日期 |
| --- | --- | --- |
| A | 新版发行 | 2019.7.22 |

1.0：一般规格（General Specification)

| 项目 Item |  | 规格/条件 Specification/Condition |  |  |
| --- | --- | --- | --- | --- |
| 1 | 型号 Mode1 No. | ## YY8025H24B-HH |  |  |
| 2 | 外型尺寸 Outline. Dimension | ## 80*25mm |  |  |
| 3 | 工作电压 Operating Voltage | DC14～27.6V |  |  |
| 4 | 额定电压 Rated .voltage | DC 24V |  |  |
| 5 | 启动电压Starting Voltage | DC ≤14V on/off |  |  |
| 6 | 额定电流 Rated current | 0.11.A(Max:0.14A) | a. 额定电压Rated .voltage b.25℃ 65% RH c.After testing for 5 minutes |  |
| 7 | 消耗功率 Power consumption | 2.31W(Max:3.36W) |  |  |
| 8 | 转速Speed | 3500±10%RPM |  |  |
| 9 | 风量Airflow AT ZERO STATIC PRESSURE | 41.09CFM(Min：36.98CFM) | a. 额定电压Rated .voltage b. AMCA标准Standard C. 额定电流Rated current |  |
|  | 静压Air .Static Pressure AT ZERO AIRFLOW | 6.61mmH2O (Min：5.95mmH2O) |  |  |
| 10 | 噪音标准Noise Level | 37.6dB-A(Max：41.36dB-A) | a. 额定电压 Rated Voltage b. 18dB无响室 18dB Non-Echo Chamber c. 标准 Standard: CNS 8753 / ISO 3744 d. Test Condition :ISO 7779 e. 距离 Distance: 1.0 M |  |
| 11 | 期望寿命Life expectancy | 70000 hrs at temp40℃ Humidity5%～95% | MTTF Mean Time To Failure Conf. Level 90% |  |
| 12 | 扇叶数No.of.Blade | 7叶 |  |  |
| 13 | 极数No.of.Pole | 4极 |  |  |
| 14 | 运转方向Rotating Direction | 顺时针/运转方向是从标签面看 |  |  |
| 15 | 锁住保护Lock Protection | 1.额定电压下堵住2～3秒,风扇自动断电,停止运转, 降低内部温升 Auto power off after locked at rated voltage for 2～3 sec. Reduce internal temperature rise 2.风扇停转后,风扇会在2至6秒自动尝试启动 After auto power off, circuit attempt to restart in 2 to 6 sec. |  |  |
| 16 | 极性保护Polarity Protection | VCC与GND反接时 不导通 Open circuit when Vcc & GND are exchanged |  |  |
| 17 | 过流保护 Over current protection | 无 NO |  |  |
| 18 | 恒速功能fixed constant speed Function | 无 NO |  |  |
| 19 | 软启动Soft Starting | 无 NO |  |  |
| 20 | PWM功能 PWM function | 无 NO |  |  |
| 21 | PQ曲线 PQ curve |  |  |  |

2.0:主要材料/零件规格（Main Materials/parts Specification）

| 材料/零件 Materials/parts |  | 规格 Specification |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 塑料材料/ 外框扇叶 Plastic Material/ Frame impeller | PBT黑色三角支架 防火等级94V-0 |  |  |  |  |
|  |  | PBT黑色7叶 防火等级94V-0 |  |  |  |  |
| 2 | 轴承 Bearing Type | 滚珠轴承 Ball Bearing |  |  |  |  |
| 3 | 引线 Lead Wire | UL1007#26#黑红分线 |  |  |  |  |
| 4 | 端子 Connector | 无端-2P |  |  |  |  |
|  |  | 黑 | 红 |  |  |  |
|  |  | GND | VCC |  |  |  |
| 5 | 环保要求 EnvironmentalRequirement |  |  | 永亿豪环保 标准 |  |  |

3.0电性规格（Electrical  Specifically）

| 1 | 绝缘阻抗 Insulation Resistance | 10MΩ/裸线与外框间测量，500VDC/min 10MΩ/between unshackled wire and frame at 500VDC/min |  |
| --- | --- | --- | --- |
| 2 | 绝缘耐压 Dielectric Strength | 5Ma Max./导线与外框间测量，500VAC/min 5Ma Max./Measured between lead wire(+)and frame at 500VAC/min |  |
| 3 | 防水等级 Waterproof level | IP XO |  |

4.0环境测试（Environmental Specification）

| 1 | 运转温/湿度范围 Operating Temp .Range | 温度/Temperature:-10℃～+70℃ 湿度/Humidity:5%～95%RH |  |
| --- | --- | --- | --- |
| 2 | 保存温/湿度范围 Storage Temperature | 温度/Temperature:-40℃～+75℃ 湿度/Humidity:5%～95%RH |  |
| 3 | 耐湿性 Humidity | 电气规格依据MIL-STD 202F Method 103B 湿度：95%RH 温度：40±2℃ |  |
| 4 | 热冲击 Thermal Shock | 电气规格依据MIL-STD 202F Method 107D Per MIL-STD 202F Method 107D,Condition D |  |
| 5 | 绝缘阶段 Insulation Shock | UL: A级 UL：Class A |  |
| 6 | 包装耐振动试验 Packing Vibration Test | 包装后，XYZ三方向施3.2G load vibration test for 30min .No serious damage |  |
| 7 | 包装耐冲击试验 Packing Shock Proof Test | 捆包后，高60公分，1棱角3边6面自然落下，无严重损坏. 1comer,3edges, 6faces natural drop from 60cm high packing No serious damage |  |

5.0在无响室额定电压下之噪音测试

（Noise is measured at rated voltage in anechoic）

（在背景噪音不超过18dB（A）的无响室内，将待测风扇通入额定的工作电压，悬掉入空中，将麦克风放于风扇同一平面且离待测风扇进风口一米处进行测试其 B&K 值） Noise is measured rated voItage in free air in anechoic chamber with B&K sound IeveI meter with microphone at a distance of one meter from the fan intake.The background noise is 18Db(A) max。

注意事项（NOTES）

1 Before use, make sure the supply voltage to meet the use of the product range, line-powered load exceeds the maximum power consumption of this product 120%. And the voltage is stable without clutter

（使用前，确认供电电压能满足本产品的使用范围，供电电路负载超过本产品的最大功耗的120%。且电压是稳定不含杂波干扰）

2 Please when ventilator circular telegram normal work do not use the hand to bump touches fan blade border

（请在风扇通电正常运转时不要用手碰触扇叶边沿）

3 Please do not touch the impeller and never carry the fan the lead wires.The bearings and the lead wires may be damaged. Additionally, static electricity may damage the intemal ciruits of the fan

(请不要碰触扇叶和拉扯线材，以免损坏轴承及导线。此外,静电可能损坏内部的风扇组件)

4 Please do not use the fan in the environment of corrosive gas or liquid.

（请不要将风扇置于腐蚀的气体和液体内）

5 Please do not store the an in the environmet of high humidity.Please avoid storage of the fan over 6months.For long term storage, please connect power to the fan shortly every 6 months even through the fan is stored in room temperature.

（请不要将风扇储存在高湿度的环境中，请尽量避免将风扇储存期超过6个月。如果要长期储存，请将其在室温的环境下。且每隔6个月须上电源让风扇短时间运转。）